## BENCHMARK PLATINUM w EDGEii_OLD
[11 empty] | AERCO Benchmark Platinum with Edge Series Boiler Schedules | [13 empty] | VERSION 2.4__
[11 empty] | Select Boiler | BMK PLATINUM 4000 w/ EDGE[ii]
BOILER SCHEDULE
[6 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/80 DEG F RWT) | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN-MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | BLOWER MOTOR HP | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NUMBER | MANUFACTURE | MODEL
B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 3480/3840 | 95 | 100 | 75 | 150 PSI | 160 | -- | -- | 35 / 500 | 5.0 PSIG @ 475GPM | NATURAL GAS | 4000 | 4 - 14 | 208/3/60 460/3/60 | 23 12 | 11 11 | 80 x 34 x 79 | 2820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 4000 WITH EDGE[ii]
NOTES:
1. VENTLESS GAS TRAIN |  |  |  | 8. COMBUSTION O2 LEVELS SHALL NOT EXCEED 7% THROUGHOUT ENTIRE FIRING RANGE. COMBUSTION SYSTEM SHALL BE CAPABLE OF O2 TRIM IN ORDER TO SELF-CALIBRATE COMBUSTION SETTINGS TO COMPENSATE FOR CHANGING CONDITIONS WHICH CAN IMPACT EFFICIENCY, MAINTENANCE, AND SAFETY FACTORS |  |  |  | 10. BOILER MANUFACTURE TO PROVIDE LOCAL PEER TO PEER BLUETOOTH COMMUNICATION TO TABLET/SMART PHONE APP TO ALLOW COMPLETE CONTROL AND SETUP OF UNIT WITH A 15-FOOT PROXIMITY |  |  | 13. PROVIDE CHECK VALVE FOR EACH INLET CONNECTION |  |  | 17. BOILER MANUFACTURE TO PROVIDE 5- YEAR NON-PRORATED BURNER WARRANTY |  |  | 20. BOILER MANUFACTURE TO MODULATE PRIMARY PUMP TO MAINTAIN OPTIMIZE BOILER EFFICIENCY |  |  | 23. BOILER MANUFACTURE CONROLLER LOGIC TO INCLUDE SWITCHING FROM MANAGER BOILER TO A BACKUP MANAGER BOILER AUTOMATICALLY. |  |  | 26. ALTERNATE MANUFACTURES MUST COMPLY WITH ALL BASIS OF DESIGN PERFORMANCE, SAFETY, DURABILITY WARRANTY AND SYSTEM DESIGN REQUIREMENTS
2. MINIMUM TURNDOWN: 15:1 | [10 empty] | 14. THE BOILER MUST HAVE A FACTORY INSTALLED DUAL RETURN SYSTEM TO INCREASE THE PLANT EFFICIENCY
4. BOILER SHALL BE CAPABLE OF UTILIZING NON-METALLIC VENT | [13 empty] | 18. BOILER MANUFACTURE TO PROVIDE 3- YEAR NON-PRORATED CONTROLLER WARRANTY |  |  | 21. PROVIDE CONDENSATE NEUTRALIZER FOR EACH BOILER AND COMMON FLUE DRAINS |  |  | 24. BOILER MANUFACTURE TO PROVIDE INTEGRATED FLOW BALANCING BETWEEN BOILERS INSTALLED IN THE BOILER PLANT
5. BMK COMMUNICATION: INTEGRATED BACNET | [7 empty] | 11. BOILER STAGING POINT NOT TO EXCEED 40% |  |  | 15. BOILER MANUFACTURE TO PROVIDE 15- YEAR NON-PRORATED HEAT EXCHANGER WARRANTY
6. PROVIDE BOILER SEQUENCING WITH HW RESET |  |  |  | 9. 5-YEAR ONAER REMOTE MONITORING AND ALERTING CONNECTED TO INTERNET VIA HARDLINE OR WI-FI COMMUNICATION MODULE |  |  |  | 12. BOILER MANUFACTURER TO PROVIDE AND CONTROL, FIELD INSTALLED, MODULATING MOTORIZED VALVES ON EACH BOILER | [5 empty] | 19. BOILER MANUFACTURE TO PROVIDE LETTER OF GUARANTEE FOR AS BUILT FLUE AND COMBUSTION AIR INSTALLATION |  |  | 22. THE BOILERS SHALL HAVE AN O2 TRIM SYSTEM WITH ACTIVE DEW-POINT CONTROL FACTORY INSTALLED. |  |  | 25. BOILER MANUFACTURE TO PROVIDE INTEGRATED O2 SENSOR AND LOGIC TO AUTOMATICALLY COMBUSTION CALIBRATE POINTS IN CONTROLLER WITH START-UP TECHNICIAN APPROVAL
7. CONTROLLER SHALL DISPLAY AN ALERT WHEN O2 LEVEL IS ABOVE OR BELOW CRITICAL VALUES. | [10 empty] | 16. BOILER MANUFACTURE TO PROVIDE ONBOARD TOUCH SCREEN WITH BUTTON BACK-UP
Schedule Selector Instructions: Step 1: Select "CLICK HERE TO SELECT REQUIRED BOILER SIZE" and use the drop down menu to select the appropriate boiler model number. Step 2: The schedule will auto populate, any cell with RED text requires editing. Notes in RED are optional. Step 3: Copy and paste the completed schedule into the program of your choice. | [13 empty] | Relief Valve Selection Tool:
Operating Pressure = System Design Pressure
Relief Valve Pressure = 20% higher than the Operating Pressure rounded up to the nearest valve rating
Boiler Pressure Rating = Maximum allowable vessel pressure per ASME standards
[14 empty] | Operating Pressure: |  | 100 | <-- Insert Operating Pressure
[14 empty] | Relief Valve Pressure: |  | 150 PSI |  | 120

## BENCHMARK PLATINUM w EDGEii
[10 empty] | AERCO Benchmark Platinum with EDGE[ii] Series Boiler Schedules | [14 empty] | VERSION 2.4__
[11 empty] | Select Boiler | BMK PLATINUM 6000 w/ EDGE[ii]
BOILER SCHEDULE
[6 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/80 DEG F RWT) | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN-MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | BLOWER MOTOR HP | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NUMBER | MANUFACTURE | MODEL
B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 5220 / 5670 | 94.5 | 100 | 110 | 150 PSI | 80 150 | -- | -- | 75 / 600 | 4.0 PSIG @ 500 GPM | NATURAL GAS | 6000 | 4 - 10 14 - 56 | 208/3/60 460/3/60 575/3/60 | 19 9 7 | 5 | 108 x 35 x 79 | 3920 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 6000 WITH EDGE[ii]
NOTES:
1. VENTLESS GAS TRAIN |  |  |  | 8. COMBUSTION O2 LEVELS SHALL NOT EXCEED 7% THROUGHOUT ENTIRE FIRING RANGE. COMBUSTION SYSTEM SHALL BE CAPABLE OF O2 TRIM IN ORDER TO SELF-CALIBRATE COMBUSTION SETTINGS TO COMPENSATE FOR CHANGING CONDITIONS WHICH CAN IMPACT EFFICIENCY, MAINTENANCE, AND SAFETY FACTORS |  |  |  | 10. BOILER MANUFACTURE TO PROVIDE LOCAL PEER TO PEER BLUETOOTH COMMUNICATION TO TABLET/SMART PHONE APP TO ALLOW COMPLETE CONTROL AND SETUP OF UNIT WITH A 15-FOOT PROXIMITY |  |  | 13. PROVIDE CHECK VALVE FOR EACH INLET CONNECTION |  |  | 17. BOILER MANUFACTURE TO PROVIDE 5- YEAR NON-PRORATED BURNER WARRANTY |  |  | 20. BOILER MANUFACTURE TO MODULATE PRIMARY PUMP TO MAINTAIN OPTIMIZE BOILER EFFICIENCY |  |  | 23. BOILER MANUFACTURE CONTROLLER LOGIC TO INCLUDE SWITCHING FROM MANAGER BOILER TO A BACKUP MANAGER BOILER AUTOMATICALLY. |  |  | 26. ALTERNATE MANUFACTURES MUST COMPLY WITH ALL BASIS OF DESIGN PERFORMANCE, SAFETY, DURABILITY WARRANTY AND SYSTEM DESIGN REQUIREMENTS
2. MINIMUM TURNDOWN: 15:1 | [10 empty] | 14. THE BOILER MUST HAVE A FACTORY INSTALLED DUAL RETURN SYSTEM TO INCREASE THE PLANT EFFICIENCY
4. BOILER SHALL BE CAPABLE OF UTILIZING NON-METALLIC VENT | [13 empty] | 18. BOILER MANUFACTURE TO PROVIDE 3- YEAR NON-PRORATED CONTROLLER WARRANTY |  |  | 21. PROVIDE CONDENSATE NEUTRALIZER FOR EACH BOILER AND COMMON FLUE DRAINS |  |  | 24. BOILER MANUFACTURE TO PROVIDE INTEGRATED FLOW BALANCING BETWEEN BOILERS INSTALLED IN THE BOILER PLANT
5. BMK COMMUNICATION: INTEGRATED BACNET | [7 empty] | 11. BOILER STAGING POINT NOT TO EXCEED 40% |  |  | 15. BOILER MANUFACTURE TO PROVIDE 15- YEAR NON-PRORATED HEAT EXCHANGER WARRANTY
6. PROVIDE BOILER SEQUENCING WITH HW RESET |  |  |  | 9. 5-YEAR ONAER REMOTE MONITORING AND ALERTING CONNECTED TO INTERNET VIA HARDLINE OR WI-FI COMMUNICATION MODULE |  |  |  | 12. BOILER MANUFACTURER TO PROVIDE AND CONTROL, FIELD INSTALLED, MODULATING MOTORIZED VALVES ON EACH BOILER | [5 empty] | 19. BOILER MANUFACTURE TO PROVIDE LETTER OF GUARANTEE FOR AS BUILT FLUE AND COMBUSTION AIR INSTALLATION |  |  | 22. THE BOILERS SHALL HAVE AN O2 TRIM SYSTEM WITH ACTIVE DEW-POINT CONTROL FACTORY INSTALLED. |  |  | 25. BOILER MANUFACTURE TO PROVIDE INTEGRATED O2 SENSOR AND LOGIC TO AUTOMATICALLY COMBUSTION CALIBRATE POINTS IN CONTROLLER WITH START-UP TECHNICIAN APPROVAL
7. CONTROLLER SHALL DISPLAY AN ALERT WHEN O2 LEVEL IS ABOVE OR BELOW CRITICAL VALUES. | [10 empty] | 16. BOILER MANUFACTURE TO PROVIDE ONBOARD TOUCH SCREEN WITH BUTTON BACK-UP
Schedule Selector Instructions: Step 1: Select "CLICK HERE TO SELECT REQUIRED BOILER SIZE" and use the drop down menu to select the appropriate boiler model number. Step 2: The schedule will auto populate, any cell with RED text requires editing. Notes in RED are optional. Step 3: Copy and paste the completed schedule into the program of your choice. | [13 empty] | Relief Valve Selection Tool:
Operating Pressure = System Design Pressure
Relief Valve Pressure = 20% higher than the Operating Pressure rounded up to the nearest valve rating
Boiler Pressure Rating = Maximum allowable vessel pressure per ASME standards
[14 empty] | Operating Pressure: |  | 100 | <-- Insert Operating Pressure
[14 empty] | Relief Valve Pressure: |  | 150 PSI |  | 120

## BENCHMARK STANDARD w EDGEi
[10 empty] | AERCO Benchmark Standard with EDGE[i] Series Boiler Schedules | [14 empty] | VERSION 2.4__
[11 empty] | Select Boiler | BMK STANDARD 6000 w/ EDGE[i]
BOILER SCHEDULE
[6 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/80 DEG F RWT) | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN-MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | BLOWER MOTOR HP | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NUMBER | MANUFACTURE | MODEL
B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 5220 / 5670 | 94.5 | 100 | 110 | 150 PSI | 80 150 | -- | -- | 75 / 600 | 4.0 PSIG @ 500 GPM | NATURAL GAS | 6000 | 4 - 10 14 - 56 | 208/3/60 460/3/60 575/3/60 | 19 9 7 | 5 | 108 x 35 x 79 | 3920 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 6000 WITH EDGE[i]
NOTES:
1. VENTLESS GAS TRAIN |  |  | 6. COMBUSTION O2 LEVELS SHALL NOT EXCEED 7% THROUGHOUT ENTIRE FIRING RANGE. |  |  | 8. PROVIDE BOILER SEQUENCING WITH HW RESET |  |  | 11. BOILER MANUFACTURE TO PROVIDE 10- YEAR NON-PRORATED HEAT EXCHANGER WARRANTY |  |  | 13. BOILER MANUFACTURE TO PROVIDE LETTER OF GUARANTEE FOR AS BUILT FLUE AND COMBUSTION AIR INSTALLATION |  |  | 15. ALTERNATE MANUFACTURES MUST COMPLY WITH ALL BASIS OF DESIGN PERFORMANCE, SAFETY, DURABILITY WARRANTY AND SYSTEM DESIGN REQUIREMENTS
2. MINIMUM TURNDOWN: 15:1 | [5 empty] | 9. BOILER SHALL BE EQUIPPED WITH COMBUSTION AIR TEMPERATURE COMPENSATION TO AUTOMATICALLY COMPENSATE FOR AIR DENSITY CHANGES BY ADJUSTING OXYGEN AND OPTIMIZE THE COMBUSTION EFFICIENCY UNDER ALL SEASONAL TEMPERATURE CHANGES.
4. BOILER SHALL UTILIZIE NON-METALLIC VENT | [8 empty] | 12. BOILER MANUFACTURE TO PROVIDE 2- YEAR NON-PRORATED CONTROLLER WARRANTY |  |  | 14. PROVIDE CONDENSATE NEUTRALIZER FOR EACH BOILER AND COMMON FLUE DRAINS
5. CONTROLLER SHALL DISPLAY AN ALERT WHEN O2 LEVEL IS ABOVE OR BELOW CRITICAL VALUES. |  |  | 7. BOILER MANUFACTURER TO PROVIDE AND CONTROL, FIELD INSTALLED, MOTORIZED ISOLATION VALVES ON EACH BOILER
10. BOILER STAGING POINT NOT TO EXCEED 40%
Schedule Selector Instructions: Step 1: Select "CLICK HERE TO SELECT REQUIRED BOILER SIZE" and use the drop down menu to select the appropriate boiler model number. Step 2: The schedule will auto populate, any cell with RED text requires editing. Notes in RED are optional. Step 3: Copy and paste the completed schedule into the program of your choice. | [13 empty] | Relief Valve Selection Tool:
Operating Pressure = System Design Pressure
Relief Valve Pressure = 20% higher than the Operating Pressure rounded up to the nearest valve rating
Boiler Pressure Rating = Maximum allowable vessel pressure per ASME standards
[14 empty] | Operating Pressure: |  | 100 | <-- Insert Operating Pressure
[14 empty] | Relief Valve Pressure: |  | 150 PSI |  | 120

## BENCHMARK w EDGEii
[10 empty] | AERCO Benchmark with EDGE[ii] Series Boiler Schedules | [14 empty] | VERSION 2.4__
[11 empty] | Select Boiler | BMK 6000 w/ EDGE[ii]
BOILER SCHEDULE
[6 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/80 DEG F RWT) | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN-MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | BLOWER MOTOR HP | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NUMBER | MANUFACTURE | MODEL
B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 5220 / 5670 | 94.5 | 100 | 110 | 150 PSI | 80 150 | -- | -- | 75 / 600 | 4.0 PSIG @ 500 GPM | NATURAL GAS | 6000 | 4 - 10 14 - 56 | 208/3/60 460/3/60 575/3/60 | 19 9 7 | 5 | 108 x 35 x 79 | 3920 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 6000 WITH EDGE[ii]
NOTES:
1. VENTLESS GAS TRAIN |  |  |  | 8. COMBUSTION O2 LEVELS SHALL NOT EXCEED 7% THROUGHOUT ENTIRE FIRING RANGE. COMBUSTION SYSTEM SHALL BE CAPABLE OF O2 TRIM IN ORDER TO SELF-CALIBRATE COMBUSTION SETTINGS TO COMPENSATE FOR CHANGING CONDITIONS WHICH CAN IMPACT EFFICIENCY, MAINTENANCE, AND SAFETY FACTORS |  |  |  | 10. BOILER MANUFACTURE TO PROVIDE LOCAL PEER TO PEER BLUETOOTH COMMUNICATION TO TABLET/SMART PHONE APP TO ALLOW COMPLETE CONTROL AND SETUP OF UNIT WITH A 15-FOOT PROXIMITY |  |  | 13. PROVIDE CHECK VALVE FOR EACH INLET CONNECTION |  |  | 17. BOILER MANUFACTURE TO PROVIDE 5- YEAR NON-PRORATED BURNER WARRANTY |  |  | 20. BOILER MANUFACTURE TO MODULATE PRIMARY PUMP TO MAINTAIN OPTIMIZE BOILER EFFICIENCY |  |  | 23. BOILER MANUFACTURE CONTROLLER LOGIC TO INCLUDE SWITCHING FROM MANAGER BOILER TO A BACKUP MANAGER BOILER AUTOMATICALLY. |  |  | 26. ALTERNATE MANUFACTURES MUST COMPLY WITH ALL BASIS OF DESIGN PERFORMANCE, SAFETY, DURABILITY WARRANTY AND SYSTEM DESIGN REQUIREMENTS
2. MINIMUM TURNDOWN: 15:1 | [10 empty] | 14. THE BOILER MUST HAVE A FACTORY INSTALLED DUAL RETURN SYSTEM TO INCREASE THE PLANT EFFICIENCY
4. BOILER SHALL BE CAPABLE OF UTILIZING NON-METALLIC VENT | [13 empty] | 18. BOILER MANUFACTURE TO PROVIDE 3- YEAR NON-PRORATED CONTROLLER WARRANTY |  |  | 21. PROVIDE CONDENSATE NEUTRALIZER FOR EACH BOILER AND COMMON FLUE DRAINS |  |  | 24. BOILER MANUFACTURE TO PROVIDE INTEGRATED FLOW BALANCING BETWEEN BOILERS INSTALLED IN THE BOILER PLANT
5. BMK COMMUNICATION: INTEGRATED BACNET | [7 empty] | 11. BOILER STAGING POINT NOT TO EXCEED 40% |  |  | 15. BOILER MANUFACTURE TO PROVIDE 15- YEAR NON-PRORATED HEAT EXCHANGER WARRANTY
6. PROVIDE BOILER SEQUENCING WITH HW RESET |  |  |  | 9. 5-YEAR ONAER REMOTE MONITORING AND ALERTING CONNECTED TO INTERNET VIA HARDLINE OR WI-FI COMMUNICATION MODULE |  |  |  | 12. BOILER MANUFACTURER TO PROVIDE AND CONTROL, FIELD INSTALLED, MODULATING MOTORIZED VALVES ON EACH BOILER | [5 empty] | 19. BOILER MANUFACTURE TO PROVIDE LETTER OF GUARANTEE FOR AS BUILT FLUE AND COMBUSTION AIR INSTALLATION |  |  | 22. THE BOILERS SHALL HAVE AN O2 TRIM SYSTEM WITH ACTIVE DEW-POINT CONTROL FACTORY INSTALLED. |  |  | 25. BOILER MANUFACTURE TO PROVIDE INTEGRATED O2 SENSOR AND LOGIC TO AUTOMATICALLY COMBUSTION CALIBRATE POINTS IN CONTROLLER WITH START-UP TECHNICIAN APPROVAL
7. CONTROLLER SHALL DISPLAY AN ALERT WHEN O2 LEVEL IS ABOVE OR BELOW CRITICAL VALUES. | [10 empty] | 16. BOILER MANUFACTURE TO PROVIDE ONBOARD TOUCH SCREEN WITH BUTTON BACK-UP
Schedule Selector Instructions: Step 1: Select "CLICK HERE TO SELECT REQUIRED BOILER SIZE" and use the drop down menu to select the appropriate boiler model number. Step 2: The schedule will auto populate, any cell with RED text requires editing. Notes in RED are optional. Step 3: Copy and paste the completed schedule into the program of your choice. | [13 empty] | Relief Valve Selection Tool:
Operating Pressure = System Design Pressure
Relief Valve Pressure = 20% higher than the Operating Pressure rounded up to the nearest valve rating
Boiler Pressure Rating = Maximum allowable vessel pressure per ASME standards
[14 empty] | Operating Pressure: |  | 100 | <-- Insert Operating Pressure
[14 empty] | Relief Valve Pressure: |  | 150 PSI |  | 120

## MFC SERIES
[12 empty] | AERCO MFC Series Boiler Schedules | [12 empty] | VERSION 2.4__
[11 empty] | Select Boiler | MFC 8000
BOILER SCHEDULE
[6 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/100 DEG F RWT) | EFFICIENCY (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN-MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | HP BLOWER MOTOR/ OIL PUMP | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NUMBER | MANUFACTURE | MODEL
B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 6872 / 7416 | 92 | 100 | 898 | 150 PSI | 80 | -- | -- | 53 / 1000 | 1.1 PSIG @ 800 GPM | NAT. GAS/ #2 FUEL OIL | 8000 | 28 - 56 | 208/3/60 460/3/60 575/3/60 | 25.8 11.7 10.2 | 7.5 / 2.0 | 220 x 71 x 102 | 24134 | UL/FM/CSD-1 | MH61241 | AERCO | MFC 8000
NOTES:
1. VENTLESS GAS TRAIN |  |  | 4. PROVIDE BOILER SEQUENCER WITH HW RESET, RUNTIME EQUALIZATION, AND MODBUS BAS COMMUNICATION |  |  | 6. BOILER MANUFACTURE TO PROVIDE 5-YEAR NON-PRORATED HEAT EXCHANGER WARRANTY |  |  | 8. ALTERNATE MANUFACTURES MUST COMPLY WITH ALL BASIS OF DESIGN PERFORMANCE, SAFETY, DURABILITY WARRANTY AND SYSTEM DESIGN REQUIREMENTS
2. MAX NOX: 40 PPM, 3% O2 CORRECTED
3. COMBUSTION O2 LEVELS SHALL NOT EXCEED 6% THROUGHOUT ENTIRE FIRING RANGE. |  |  | 5. THE BOILER MUST HAVE A FACTORY INSTALLED DUAL RETURN SYSTEM TO INCREASE THE PLANT EFFICIENCY |  |  | 7. BOILER MANUFACTURE TO PROVIDE LETTER OF GUARANTEE FOR AS BUILT FLUE AND COMBUSTION AIR INSTALLATION |  |  | 9. PROVIDE CONDENSATE NEUTRALIZER FOR EACH BOILER AND COMMON FLUE DRAINS
Schedule Selector Instructions: Step 1: Select "CLICK HERE TO SELECT REQUIRED BOILER SIZE" and use the drop down menu to select the appropriate boiler model number. Step 2: The schedule will auto populate, any cell with RED text requires editing. Notes in RED are optional. Step 3: Copy and paste the completed schedule into the program of your choice. | [13 empty] | Relief Valve Selection Tool:
Operating Pressure = System Design Pressure
Relief Valve Pressure = 20% higher than the Operating Pressure rounded up to the nearest valve rating
Boiler Pressure Rating = Maximum allowable vessel pressure per ASME standards
[14 empty] | Operating Pressure: |  | 100 | <-- Insert Operating Pressure
[14 empty] | Relief Valve Pressure: |  | 150 PSI |  | 120

## AM SERIES
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
[12 empty] | AERCO AM Series Boiler Schedules | [11 empty] | VERSION 2.4__
[11 empty] | Select Boiler | AM 1000
BOILER SCHEDULE
[8 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
| UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/60 DEG F RWT) | NUMBER OF BURNER MODULES | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP AT MAX FLOW (FT. HD.) | FUEL | GAS INPUT (CFH) | MIN/MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | MANUFACTURE | MODEL
| B-1..B-X | MER | HEATING | CONDENSING WATER TUBE | 874 / 971 | 4 | 93.8 | -- | 9 | 50 | 160 | -- | -- | 18 / 80 | 47 | NATURAL GAS | 1000 | 3 / 13 | 120/1/60 | 4.9 | 35.3 X 23.6 X 71.3 | 615 | CSA/CSD-1 | AERCO | AM 1000
NOTES:
| 1. INTEGRAL CONDENSATE NEUTRALIZATION |  |  | 5. COMBUSTION O2 LEVELS SHALL NOT EXCEED 7% THROUGHOUT ENTIRE FIRING RANGE. |  |  | 8. BOILER MANUFACTURE TO PROVIDE 7- YEAR NON-PRORATED HEAT EXCHANGER WARRANTY |  |  | 10. BOILER MANUFACTURE TO PROVIDE LETTER OF GUARANTEE FOR AS BUILT FLUE AND COMBUSTION AIR INSTALLATION
2. MINIMUM TURNDOWN: 20:1
| 3. MAX NOX: 20 PPM, 3% O2 CORRECTED |  |  | 6. AM BOILER COMMUNICATION: INTEGRATED MODBUS |  |  | 9. MANUFACTURER TO INCLUDE INSTALLATION KIT CONTAINING: BOILER PUMP, CIRCUIT SETTER, STRAINER & ISOLATION VALVE |  |  | 11. ALTERNATE MANUFACTURERS MUST COMPLY WITH ALL PERFORMANCE, SAFETY, DURABILITY, WARRANTY, AND SYSTEM DESIGN REQUIREMENTS AS DETAILED IN CONTRACT SPECIFICATIONS.
| 4. BOILER SHALL BE CAPABLE OF UTILIZING NON-METALLIC VENT |  |  | 7. PROVIDE BOILER SEQUENCER FOR MULTIPLE BOILER INSTALLATIONS
| Schedule Selector Instructions: Step 1: Select "CLICK HERE TO SELECT REQUIRED BOILER SIZE" and use the drop down menu to select the appropriate boiler model number. Step 2: The schedule will auto populate, any cell with RED text requires editing. Step 3: Copy and paste the completed schedule into the program of your choice. | [13 empty] | Relief Valve Information:
Operating Pressure = System Design Pressure
Relief Valve Pressure = 15 PSI higher than the Operating Pressure rounded up to the nearest valve rating
Boiler Pressure Rating = Maximum allowable vessel pressure per ASME standards
All AERCO AM Boilers ship standard with 50 PSIG relief valves. For systems operating at pressures in excess of 35 PSIG the relief valves must be provided and installed by the installing contractor. The number of relief valves per boiler equals the number of burner modules (see schedule above).

## MLX EXT
[12 empty] | AERCO MLX EXT Series Boiler Schedules | [12 empty] | VERSION 2.4__
[11 empty] | Select Boiler | MLX EXT 3000 2S
BOILER SCHEDULE
[7 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/60 DEG F RWT) | NUMBER OF BURNER MODULES | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP AT MAX FLOW (FT. HD.) | FUEL | GAS INPUT (CFH) | MIN/MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NUMBER | MANUFACTURE | MODEL
B-1..B-X | MER | HEATING | CAST AL | 2687 / 2831 | 8 | 92 | -- | 7 | 80 | 92 | -- | -- | 113 / 225 | 13.2 FT.HD. @ 225 GPM | NATURAL GAS | 3060 | 4 - 10.5 | 120/1/60 | 20 | 38.3 x 63.9 x 57.2 | 1664 | UL/FM/CSD-1 | MH49893 | AERCO | MLX EXT 3000 2S
NOTES:
1. VENTLESS GAS TRAIN |  |  | 5.BOILER SHALL BE RATED FOR OUTDDOR INSTALLATION. |  |  | 9. BOILER STAGING POINT NOT TO EXCEED 20% |  |  | 12. BOILER MANUFACTURE TO PROVIDE LETTER OF GUARANTEE FOR AS BUILT FLUE AND COMBUSTION AIR INSTALLATION |  |  | 14. ALTERNATE MANUFACTURES MUST COMPLY WITH ALL BASIS OF DESIGN PERFORMANCE, SAFETY, DURABILITY WARRANTY AND SYSTEM DESIGN REQUIREMENTS
2. MINIMUM TURNDOWN: 39:1 |  |  | 6. COMBUSTION O2 LEVELS SHALL NOT EXCEED 6% THROUGHOUT ENTIRE FIRING RANGE. |  |  | 10. BOILER MANUFACTURE TO PROVIDE 10- YEAR NON-PRORATED HEAT EXCHANGER WARRANTY
3. MAX NOX: 20 PPM, 3% O2 CORRECTED | [8 empty] | 13. PROVIDE CONDENSATE NEUTRALIZER FOR EACH BOILER AND COMMON FLUE DRAINS
4. BOILER SHALL BE CAPABLE OF UTILIZING NON-METALLIC VENT |  |  | 7. MLX EXT COMMUNICATION: INTEGRATED MODBUS |  |  | 11. BOILER MANUFACTURE TO PROVIDE 5- YEAR NON-PRORATED CONTROLLER WARRANTY
8. PROVIDE BOILER SEQUENCING WITH HW RESET
Schedule Selector Instructions: Step 1: Select "CLICK HERE TO SELECT REQUIRED BOILER SIZE" and use the drop down menu to select the appropriate boiler model number. Step 2: The schedule will auto populate, any cell with RED text requires editing. Notes in RED are optional. Step 3: Copy and paste the completed schedule into the program of your choice. | [13 empty] | Relief Valve Information:
Operating Pressure = System Design Pressure
Relief Valve Pressure = 15 PSI higher than the Operating Pressure rounded up to the nearest valve rating
Boiler Pressure Rating = Maximum allowable vessel pressure per ASME standards
All MLX EXT Boilers ship standard with 80 PSIG relief valves. For systems operating at pressures in excess of 65 PSIG the relief valves must be provided and installed by the installing contractor.

## Reference (hidden)
BOILER SCHEDULE
[7 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
| UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/80 DEG F RWT) | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN/MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | BLOWER MOTOR HP | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NO. | MANUFACTURE | MODEL | MINIMUM TURNDOWN | MIN Nox
CLICK HERE TO SELECT REQUIRED BOILER SIZE | B-1..B-X | MER | HEATING | -- | -- |  | -- |  | 30/50/75/100/150 | 160 | -- | -- | -- | -- | NATURAL GAS | -- | -- | -- | -- | -- | -- | -- |  | MH15883 | AERCO | -- | 2. MINIMUM TURNDOWN: -- | 3. MAX NOX: --
BMK PLATINUM 750 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 653 / 720 | 95.5 | -- | 16.25 | 30/50/75/100/150 | 160 | -- | -- | 25 / 175 | 3.0 PSIG @ 100 GPM | NATURAL GAS | 750 | 4 - 14 | 120/1/60 | 13 | 1 | 34 x 28 x 78 | 820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 750 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK PLATINUM 1000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 875 / 975 | 96.8 | -- | 14.25 | 30/50/75/100/150 | 160 | -- | -- | 25 / 175 | 3.0 PSIG @ 100 GPM | NATURAL GAS | 1000 | 4 - 14 | 120/1/60 | 13 | 1 | 34 x 28 x 78 | 820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 1000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK PLATINUM 1500 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 1305 / 1425 | 94.6 | -- | 44 | 30/50/75/100/150 | 160 | -- | -- | 25 / 250 | 3.0 PSIG @ 170 GPM | NATURAL GAS | 1500 | 4 - 14 | 120/1/60 | 16 | 1.6 | 34 x 44 x 78 | 1654 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 1500 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK PLATINUM 2000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 1740 / 1900 | 94.6 | -- | 40 | 30/50/75/100/150 | 160 | -- | -- | 25 / 350 | 3.0 PSIG @ 170 GPM | NATURAL GAS | 2000 | 4 - 14 | 120/1/60 | 16 | 1.6 | 58 x 28 x 78 | 1654 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 2000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK PLATINUM 2500 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 2175 / 2375 | 93.5 | -- | 58 | 30/50/75/100/150 | 160 | -- | -- | 25 / 350 | 3.0 PSIG @ 218 GPM | NATURAL GAS | 2500 | 4 - 14 | 208/3/60 460/3/60 | 10 5 | 3.0 3.2 | 68 x 28 x 78 | 2580 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 2500 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK PLATINUM 3000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 2625 / 2925 | 93.5 | -- | 55 | 30/50/75/100/150 | 160 | -- | -- | 25 / 375 | 3.0 PSIG @ 261 GPM | NATURAL GAS | 3000 | 4 - 14 | 208/3/60 460/3/60 | 10 5 | 3.0 3.2 | 68 x 28 x 78 | 2580 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 3000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK PLATINUM 4000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 3480/3840 | 95 | -- | 75 | 30/50/75/100/150 | 160 | -- | -- | 35 / 500 | 5.0 PSIG @ 475GPM | NATURAL GAS | 4000 | 4 - 14 | 208/3/60 460/3/60 | 23 12 | 11 11 | 80 x 34 x 79 | 2820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 4000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK PLATINUM 5000N w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 4341/4790 | 95 | -- | 75 | 30/50/75/100/150 | 160 | -- | -- | 35 / 500 | 5.0 PSIG @ 475GPM | NATURAL GAS | 4990 | 4 - 14 | 208/3/60 460/3/60 | 23 12 | 11 11 | 80 x 34 x 79 | 2820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 5000N WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK PLATINUM 5000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 4350 / 4725 | 94.5 | -- | 110 | 30/50/75/100/150 | 80 150 | -- | -- | 75 / 600 | 4.0 PSIG @ 500 GPM | NATURAL GAS | 5000 | 4 - 10 14 - 56 | 208/3/60 460/3/60 575/3/60 | 19 9 7 | 5 | 108 x 35 x 79 | 3920 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 5000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 12.5:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK PLATINUM 6000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 5220 / 5670 | 94.5 | -- | 110 | 30/50/75/100/150 | 80 150 | -- | -- | 75 / 600 | 4.0 PSIG @ 500 GPM | NATURAL GAS | 6000 | 4 - 10 14 - 56 | 208/3/60 460/3/60 575/3/60 | 19 9 7 | 5 | 108 x 35 x 79 | 3920 | UL/FM/CSD-1 | MH15883 | AERCO | BMK PLATINUM 6000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BOILER SCHEDULE
[7 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
| UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/80 DEG F RWT) | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN/MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | BLOWER MOTOR HP | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NO. | MANUFACTURE | MODEL
CLICK HERE TO SELECT REQUIRED BOILER SIZE | B-1..B-X | MER | HEATING | -- | -- |  | -- |  |  |  | -- | -- | -- | -- |  | -- | -- | -- | -- | -- | -- | -- |  | MH15883 | AERCO | -- | 2. MINIMUM TURNDOWN: -- | 3. MAX NOX: --
BMK STANDARD 750 w/ EDGE[i] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 653 / 720 | 95.5 | -- | 16.25 | 30/50/75/100/150 | 160 | -- | -- | 25 / 175 | 3.0 PSIG @ 100 GPM | NATURAL GAS | 750 | 4 - 14 | 120/1/60 | 13 | 1 | 34 x 28 x 78 | 820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 750 WITH EDGE[i] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK STANDARD 1000 w/ EDGE[i] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 875 / 975 | 96.8 | -- | 14.25 | 30/50/75/100/150 | 160 | -- | -- | 25 / 175 | 3.0 PSIG @ 100 GPM | NATURAL GAS | 1000 | 4 - 14 | 120/1/60 | 13 | 1 | 34 x 28 x 78 | 820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 1000 WITH EDGE[i] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK STANDARD 1500 w/ EDGE[i] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 1305 / 1425 | 94.6 | -- | 44 | 30/50/75/100/150 | 160 | -- | -- | 25 / 250 | 3.0 PSIG @ 170 GPM | NATURAL GAS | 1500 | 4 - 14 | 120/1/60 | 16 | 1.6 | 34 x 44 x 78 | 1654 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 1500 WITH EDGE[i] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK STANDARD 2000 w/ EDGE[i] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 1740 / 1900 | 94.6 | -- | 40 | 30/50/75/100/150 | 160 | -- | -- | 25 / 350 | 3.0 PSIG @ 170 GPM | NATURAL GAS | 2000 | 4 - 14 | 120/1/60 | 16 | 1.6 | 58 x 28 x 78 | 1654 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 2000 WITH EDGE[i] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK STANDARD 2500 w/ EDGE[i] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 2175 / 2375 | 93.5 | -- | 58 | 30/50/75/100/150 | 160 | -- | -- | 25 / 350 | 3.0 PSIG @ 218 GPM | NATURAL GAS | 2500 | 4 - 14 | 208/3/60 460/3/60 | 10 5 | 3.0 3.2 | 68 x 28 x 78 | 2580 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 2500 WITH EDGE[i] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK STANDARD 3000 w/ EDGE[i] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 2625 / 2925 | 93.5 | -- | 55 | 30/50/75/100/150 | 160 | -- | -- | 25 / 375 | 3.0 PSIG @ 261 GPM | NATURAL GAS | 3000 | 4 - 14 | 208/3/60 460/3/60 | 10 5 | 3.0 3.2 | 68 x 28 x 78 | 2580 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 3000 WITH EDGE[i] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK STANDARD 4000 w/ EDGE[i] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 3480/3840 | 95 | -- | 75 | 30/50/75/100/150 | 160 | -- | -- | 35 / 500 | 5.0 PSIG @ 475GPM | NATURAL GAS | 4000 | 4 - 14 | 208/3/60 460/3/60 | 23 12 | 11 11 | 80 x 34 x 79 | 2820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 4000 WITH EDGE[i] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK STANDARD 5000N w/ EDGE[i] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 4341/4790 | 95 | -- | 75 | 30/50/75/100/150 | 160 | -- | -- | 35 / 500 | 5.0 PSIG @ 475GPM | NATURAL GAS | 4990 | 4 - 14 | 208/3/60 460/3/60 | 23 12 | 11 11 | 80 x 34 x 79 | 2820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 5000N WITH EDGE[i] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK STANDARD 5000 w/ EDGE[i] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 4350 / 4725 | 94.5 | -- | 110 | 30/50/75/100/150 | 80 150 | -- | -- | 75 / 600 | 4.0 PSIG @ 500 GPM | NATURAL GAS | 5000 | 4 - 10 14 - 56 | 208/3/60 460/3/60 575/3/60 | 19 9 7 | 5 | 108 x 35 x 79 | 3920 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 5000 WITH EDGE[i] | 2. MINIMUM TURNDOWN: 12.5:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK STANDARD 6000 w/ EDGE[i] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 5220 / 5670 | 94.5 | -- | 110 | 30/50/75/100/150 | 80 150 | -- | -- | 75 / 600 | 4.0 PSIG @ 500 GPM | NATURAL GAS | 6000 | 4 - 10 14 - 56 | 208/3/60 460/3/60 575/3/60 | 19 9 7 | 5 | 108 x 35 x 79 | 3920 | UL/FM/CSD-1 | MH15883 | AERCO | BMK STANDARD 6000 WITH EDGE[i] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BOILER SCHEDULE
[7 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
| UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/80 DEG F RWT) | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN/MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | BLOWER MOTOR HP | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NO. | MANUFACTURE | MODEL | MINIMUM TURNDOWN | MIN Nox
CLICK HERE TO SELECT REQUIRED BOILER SIZE | B-1..B-X | MER | HEATING | -- | -- |  | -- |  | 30/50/75/100/150 | 160 | -- | -- | -- | -- | NATURAL GAS | -- | -- | -- | -- | -- | -- | -- |  | MH15883 | AERCO | -- | 2. MINIMUM TURNDOWN: -- | 3. MAX NOX: --
BMK 750 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 653 / 720 | 95.5 | -- | 16.25 | 30/50/75/100/150 | 160 | -- | -- | 25 / 175 | 3.0 PSIG @ 100 GPM | NATURAL GAS | 750 | 4 - 14 | 120/1/60 | 13 | 1 | 34 x 28 x 78 | 820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 750 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK 1000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 875 / 975 | 96.8 | -- | 14.25 | 30/50/75/100/150 | 160 | -- | -- | 25 / 175 | 3.0 PSIG @ 100 GPM | NATURAL GAS | 1000 | 4 - 14 | 120/1/60 | 13 | 1 | 34 x 28 x 78 | 820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 1000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK 1500 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 1305 / 1425 | 94.6 | -- | 44 | 30/50/75/100/150 | 160 | -- | -- | 25 / 250 | 3.0 PSIG @ 170 GPM | NATURAL GAS | 1500 | 4 - 14 | 120/1/60 | 16 | 1.6 | 34 x 44 x 78 | 1654 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 1500 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK 2000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 1740 / 1900 | 94.6 | -- | 40 | 30/50/75/100/150 | 160 | -- | -- | 25 / 350 | 3.0 PSIG @ 170 GPM | NATURAL GAS | 2000 | 4 - 14 | 120/1/60 | 16 | 1.6 | 58 x 28 x 78 | 1654 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 2000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BMK 2500 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 2175 / 2375 | 93.5 | -- | 58 | 30/50/75/100/150 | 160 | -- | -- | 25 / 350 | 3.0 PSIG @ 218 GPM | NATURAL GAS | 2500 | 4 - 14 | 208/3/60 460/3/60 | 10 5 | 3.0 3.2 | 68 x 28 x 78 | 2580 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 2500 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK 3000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 2625 / 2925 | 93.5 | -- | 55 | 30/50/75/100/150 | 160 | -- | -- | 25 / 375 | 3.0 PSIG @ 261 GPM | NATURAL GAS | 3000 | 4 - 14 | 208/3/60 460/3/60 | 10 5 | 3.0 3.2 | 68 x 28 x 78 | 2580 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 3000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK 4000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 3480/3840 | 95 | -- | 75 | 30/50/75/100/150 | 160 | -- | -- | 35 / 500 | 5.0 PSIG @ 475GPM | NATURAL GAS | 4000 | 4 - 14 | 208/3/60 460/3/60 | 23 12 | 11 11 | 80 x 34 x 79 | 2820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 4000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK 5000N w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 4341/4790 | 95 | -- | 75 | 30/50/75/100/150 | 160 | -- | -- | 35 / 500 | 5.0 PSIG @ 475GPM | NATURAL GAS | 4990 | 4 - 14 | 208/3/60 460/3/60 | 23 12 | 11 11 | 80 x 34 x 79 | 2820 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 5000N WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK 5000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 4350 / 4725 | 94.5 | -- | 110 | 30/50/75/100/150 | 80 150 | -- | -- | 75 / 600 | 4.0 PSIG @ 500 GPM | NATURAL GAS | 5000 | 4 - 10 14 - 56 | 208/3/60 460/3/60 575/3/60 | 19 9 7 | 5 | 108 x 35 x 79 | 3920 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 5000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 12.5:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BMK 6000 w/ EDGE[ii] | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 5220 / 5670 | 94.5 | -- | 110 | 30/50/75/100/150 | 80 150 | -- | -- | 75 / 600 | 4.0 PSIG @ 500 GPM | NATURAL GAS | 6000 | 4 - 10 14 - 56 | 208/3/60 460/3/60 575/3/60 | 19 9 7 | 5 | 108 x 35 x 79 | 3920 | UL/FM/CSD-1 | MH15883 | AERCO | BMK 6000 WITH EDGE[ii] | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 30 PPM, 3% O2 CORRECTED
BOILER SCHEDULE
[8 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
| UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/60 DEG F RWT) | NUMBER OF BURNER MODULES | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP AT MAX FLOW (FT. HD.) | FUEL | GAS INPUT (CFH) | MIN/MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | MANUFACTURE | MODEL
CLICK HERE TO SELECT REQUIRED BOILER SIZE | B-1..B-X | MER | HEATING | CONDENSING WATER TUBE | -- | -- | -- | -- | -- | 50 | 160 | -- | -- | -- | -- | NATURAL GAS | -- | 3 / 13 | 120/1/60 | -- | -- | -- | CSA/CSD-1 | AERCO | -- |  | 2. MINIMUM TURNDOWN: -- |  |  | MBH input | Eff 160 return | Eff 60 return | BTU/hr to BHP conv | BHP 160 RWT | BHP 60 RWT | NET OUTPUT MBH 160 RWT | NET OUTPUT MBH 60 RWT
AM 399 | B-1..B-X | MER | HEATING | CONDENSING WATER TUBE | 349 / 387 | 2 | 93.8 | -- | 4 | 50 | 160 | -- | -- | 11 / 40 | 34 | NATURAL GAS | 399 | 3 / 13 | 120/1/60 | 1.8 | 34.8 X 23.6 X 45.7 | 300 | CSA/CSD-1 | AERCO | AM 399 |  | 2. MINIMUM TURNDOWN: 8:1 |  |  | 399 | 0.874 | 0.971 | 33471.4 | 10 | 12 | 349 | 387
AM 500 | B-1..B-X | MER | HEATING | CONDENSING WATER TUBE | 437 / 486 | 2 | 93.8 | -- | 4 | 50 | 160 | -- | -- | 12 / 40 | 40 | NATURAL GAS | 500 | 3 / 13 | 120/1/60 | 2.5 | 34.8 X 23.6 X 45.7 | 310 | CSA/CSD-1 | AERCO | AM 500 |  | 2. MINIMUM TURNDOWN: 10:1 |  |  | 500 | 0.874 | 0.971 | 33471.4 | 13 | 15 | 437 | 486
AM 750 | B-1..B-X | MER | HEATING | CONDENSING WATER TUBE | 656 / 728 | 3 | 93.8 | -- | 7 | 50 | 160 | -- | -- | 14 / 60 | 50 | NATURAL GAS | 750 | 3 / 13 | 120/1/60 | 3.6 | 35.3 X 23.6 X 71.3 | 530 | CSA/CSD-1 | AERCO | AM 750 |  | 2. MINIMUM TURNDOWN: 15:1 |  |  | 750 | 0.874 | 0.971 | 33471.4 | 20 | 22 | 656 | 728
AM 1000 | B-1..B-X | MER | HEATING | CONDENSING WATER TUBE | 874 / 971 | 4 | 93.8 | -- | 9 | 50 | 160 | -- | -- | 18 / 80 | 47 | NATURAL GAS | 1000 | 3 / 13 | 120/1/60 | 4.9 | 35.3 X 23.6 X 71.3 | 615 | CSA/CSD-1 | AERCO | AM 1000 |  | 2. MINIMUM TURNDOWN: 20:1 |  |  | 1000 | 0.874 | 0.971 | 33471.4 | 26 | 29 | 874 | 971
BOILER SCHEDULE
[7 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
| UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/100 DEG F RWT) | EFFICIENCY (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN/MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | HP BLOWER MOTOR/ OIL PUMP | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NO. | MANUFACTURE | MODEL
CLICK HERE TO SELECT REQUIRED BOILER SIZE | B-1..B-X | MER | HEATING | -- | -- | -- | -- | -- | 30/50/60/75/80 | 80 | -- | -- | -- | -- | NAT. GAS/ #2 FUEL OIL | -- | -- | -- | -- | -- | -- | -- | UL/FM/CSD-1 | MH61241 | AERCO | -- |  | 2. MAX NOX: -- |  | MBH input | Eff 160 return | Eff 100 return | BTU/hr to BHP conv | BHP 160 RWT | BHP 100 RWT | NET OUTPUT MBH 160 RWT | NET OUTPUT MBH 100 RWT
MFC 3000 | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 2577 / 2781 | 92 | -- | 407 | 30/50/60/75/80 | 80 | -- | -- | 20 / 350 | 2.4 PSIG @ 300 GPM | NAT. GAS/ #2 FUEL OIL | 3000 | 14 - 28 | 208/3/60 460/3/60 575/3/60 | 11.4 5.8 4.5 | 3.0 / 1.0 | 172 x 54 x 84 | 10694 | UL/FM/CSD-1 | MH61241 | AERCO | MFC 3000 |  | 2. MAX NOX: 30 PPM, 3% O2 CORRECTED |  | 3000 | 0.859 | 0.927 | 33471.4 | 77 | 83 | 2577 | 2781
MFC 4000 | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 3436 / 3708 | 92 | -- | 464 | 30/50/60/75/80 | 80 | -- | -- | 27 / 520 | 1.0 PSIG @ 400 GPM | NAT. GAS/ #2 FUEL OIL | 4000 | 14 - 28 | 208/3/60 460/3/60 575/3/60 | 16.8 7.6 6.2 | 7.5 / 1.0 | 174 x 59 x 88 | 14030 | UL/FM/CSD-1 | MH61241 | AERCO | MFC 4000 |  | 2. MAX NOX: 30 PPM, 3% O2 CORRECTED |  | 4000 | 0.859 | 0.927 | 33471.4 | 103 | 111 | 3436 | 3708
MFC 5000 | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 4295 / 4635 | 92 | -- | 518 | 30/50/60/75/80 | 80 | -- | -- | 33 / 610 | 1.3 PSIG @ 500 GPM | NAT. GAS/ #2 FUEL OIL | 5000 | 14 - 28 | 208/3/60 460/3/60 575/3/60 | 16.8 7.6 6.2 | 7.5 / 1.0 | 186 x 59 x 88 | 15383 | UL/FM/CSD-1 | MH61241 | AERCO | MFC 5000 |  | 2. MAX NOX: 30 PPM, 3% O2 CORRECTED |  | 5000 | 0.859 | 0.927 | 33471.4 | 128 | 138 | 4295 | 4635
MFC 6000 | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 5154 / 5562 | 92 | -- | 724 | 30/50/60/75/80 | 80 | -- | -- | 40 / 750 | 1.9 PSIG @ 600 GPM | NAT. GAS/ #2 FUEL OIL | 6000 | 28 - 56 | 208/3/60 460/3/60 575/3/60 | 16.8 7.6 6.2 | 7.5 / 1.0 | 193 x 71 x 101 | 19403 | UL/FM/CSD-1 | MH61241 | AERCO | MFC 6000 |  | 2. MAX NOX: 40 PPM, 3% O2 CORRECTED2 |  | 6000 | 0.859 | 0.927 | 33471.4 | 154 | 166 | 5154 | 5562
MFC 8000 | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 6872 / 7416 | 92 | -- | 898 | 30/50/60/75/80 | 80 | -- | -- | 53 / 1000 | 1.1 PSIG @ 800 GPM | NAT. GAS/ #2 FUEL OIL | 8000 | 28 - 56 | 208/3/60 460/3/60 575/3/60 | 25.8 11.7 10.2 | 7.5 / 2.0 | 220 x 71 x 102 | 24134 | UL/FM/CSD-1 | MH61241 | AERCO | MFC 8000 |  | 2. MAX NOX: 40 PPM, 3% O2 CORRECTED |  | 8000 | 0.859 | 0.927 | 33471.4 | 205 | 222 | 6872 | 7416
MFC 10000 | B-1..B-X | MER | HEATING | CONDENSING FIRE TUBE | 8590 / 9270 | 92 | -- | 1043 | 30/50/60/75/80 | 80 | -- | -- | 67 / 1100 | 1.7 PSIG @ 1000 GPM | NAT. GAS/ #2 FUEL OIL | 10000 | 28 - 56 | 208/3/60 460/3/60 575/3/60 | 25.8 11.7 10.2 | 7.5 / 2.0 | 240 x 71 x 102 | 27219 | UL/FM/CSD-1 | MH61241 | AERCO | MFC 10000 |  | 2. MAX NOX: 40 PPM, 3% O2 CORRECTED |  | 10000 | 0.859 | 0.927 | 33471.4 | 257 | 277 | 8590 | 9270
WATER HEATER SCHEDULE
[7 empty] | WATER DATA | [7 empty] | BURNER DATA |  |  | ELECTRICAL DATA
| UNIT NO. | LOCATION | SERVICE | WATER HEATER TYPE | NET OUTPUT (MBH) (160/80 DEG F RWT) | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | HEATER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN/MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | BLOWER MOTOR HP | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NO. | MANUFACTURE | MODEL
CLICK HERE TO SELECT REQUIRED BOILER SIZE | HW-1..HW-X | MER | DOMESTIC | -- | -- |  | -- |  | 150 | 160 | -- | -- | 0/50 | -- | NATURAL GAS | -- | -- | -- | -- | -- | -- | -- |  | MH15883 | AERCO | -- | 2. MINIMUM TURNDOWN: -- | 3. MAX NOX: -- | 3. MAX NOX: --
INN 600 | HW-1..HW-X | MER | DOMESTIC | CONDENSING FIRE TUBE | 653 / 720 | 95.5 | -- | 16.25 | 150 | 160 | -- | -- | 0/50 | 3.0 PSIG @ 100 GPM | NATURAL GAS | 750 | 4 - 14 | 120/1/60 | 13 | 1 | 34 x 28 x 78 | 820 | UL/FM/CSD-1 | MH15883 | AERCO | INN 600 | 2. MINIMUM TURNDOWN: 15:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
INN 800 | HW-1..HW-X | MER | DOMESTIC | CONDENSING FIRE TUBE | 875 / 975 | 96.8 | -- | 14.25 | 150 | 160 | -- | -- | 0/50 | 3.0 PSIG @ 100 GPM | NATURAL GAS | 1000 | 4 - 14 | 120/1/60 | 13 | 1 | 34 x 28 x 78 | 820 | UL/FM/CSD-1 | MH15883 | AERCO | INN 800 | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
INN 1060 | HW-1..HW-X | MER | DOMESTIC | CONDENSING FIRE TUBE | 1305 / 1425 | 94.6 | -- | 44 | 150 | 160 | -- | -- | 0/50 | 3.0 PSIG @ 170 GPM | NATURAL GAS | 1500 | 4 - 14 | 120/1/60 | 16 | 1.6 | 34 x 44 x 78 | 1654 | UL/FM/CSD-1 | MH15883 | AERCO | INN 1060 | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
INN 1350 | HW-1..HW-X | MER | DOMESTIC | CONDENSING FIRE TUBE | 1740 / 1900 | 94.6 | -- | 40 | 150 | 160 | -- | -- | 0/50 | 3.0 PSIG @ 170 GPM | NATURAL GAS | 2000 | 4 - 14 | 120/1/60 | 16 | 1.6 | 58 x 28 x 78 | 1654 | UL/FM/CSD-1 | MH15883 | AERCO | INN 1350 | 2. MINIMUM TURNDOWN: 20:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED
BOILER SCHEDULE
[7 empty] | WATER DATA | [8 empty] | BURNER DATA |  |  | ELECTRICAL DATA
| UNIT NO. | LOCATION | SERVICE | BOILER TYPE | NET OUTPUT (MBH) (160/80 DEG F RWT) | NUMBER OF BURNER MODULES | AHRI EFFICIENCY (BTS-2000) (%) | OPERATING PRESSURE (PSIG) | BOILER CAPACITY (GAL) | RELIEF VALVE PRESSURE (PSIG) | BOILER PRESSURE RATING (PSIG) | DESIGN DELTA T (DEG F) | DESIGN FLOW (GPM) | BOILER MIN/MAX WATER FLOW (GPM) | PRESSURE DROP | FUEL | GAS INPUT (CFH) | MIN/MAX GAS INLET PRESSURE (IN W.C.) | VOLT/PHASE/HZ | FLA | DIMENSIONS L x W x H (IN) | UNIT OPERATING WEIGHT (LBS) | APPROVAL | UL LISTING NO. | MANUFACTURE | MODEL
CLICK HERE TO SELECT REQUIRED BOILER SIZE | B-1..B-X | MER | HEATING | -- | -- | -- | -- | -- | -- | 80 | 92 | -- | -- | -- | -- | NATURAL GAS | -- | -- | -- | -- | -- | -- | UL/FM/CSD-1 | MH49893 | AERCO | -- | 2. MINIMUM TURNDOWN: -- | 3. MAX NOX: -- |  | MBH input | Eff 160 return | Eff 80 return | BTU/hr to BHP conv | BHP 160 RWT | BHP 80 RWT | NET OUTPUT MBH 160 RWT | NET OUTPUT MBH 80 RWT
MLX EXT 450 2S | B-1..B-X | MER | HEATING | CAST AL | 421 / 444 | 3 | 90 | -- | 3.8 | 80 | 92 | -- | -- | 18 / 42 | 11.8 FT.HD. @ 42 GPM | NATURAL GAS | 482 | 3.5 - 10.5 | 120/1/60 | 2.7 | 30.3 x 30 x 45.3 | 454 | UL/FM/CSD-1 | MH49893 | AERCO | MLX EXT 450 2S | 2. MINIMUM TURNDOWN: 10.5:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED |  | 481.5 | 0.875 | 0.922 | 33471.4 | 13 | 13 | 421 | 444
MLX EXT 600 2S | B-1..B-X | MER | HEATING | CAST AL | 562 / 592 | 4 | 90 | -- | 4.9 | 80 | 92 | -- | -- | 24 / 56 | 9.2 FT.HD. @ 56 GPM | NATURAL GAS | 642 | 3.5 - 10.5 | 120/1/60 | 3.6 | 30.3 x 40.6 x 45.3 | 568 | UL/FM/CSD-1 | MH49893 | AERCO | MLX EXT 600 2S | 2. MINIMUM TURNDOWN: 14:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED |  | 642 | 0.875 | 0.922 | 33471.4 | 17 | 18 | 562 | 592
MLX EXT 800 2S | B-1..B-X | MER | HEATING | CAST AL | 702 / 740 | 5 | 90 | -- | 5.9 | 80 | 92 | -- | -- | 30 / 71 | 9.7 FT.HD. @ 71 GPM | NATURAL GAS | 802 | 3.5 - 10.5 | 120/1/60 | 4.5 | 30.3 x 40.6 x 45.3 | 634 | UL/FM/CSD-1 | MH49893 | AERCO | MLX EXT 800 2S | 2. MINIMUM TURNDOWN: 17.5:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED |  | 802.5 | 0.875 | 0.922 | 33471.4 | 21 | 22 | 702 | 740
MLX EXT 1100 2S | B-1..B-X | MER | HEATING | CAST AL | 983 / 1036 | 7 | 90 | -- | 8 | 80 | 92 | -- | -- | 42 / 99 | 9.5 FT.HD. @ 99 GPM | NATURAL GAS | 1124 | 3.5 - 10.5 | 120/1/60 | 6.3 | 30.3 x 51.2 x 45.3 | 826 | UL/FM/CSD-1 | MH49893 | AERCO | MLX EXT 1100 2S | 2. MINIMUM TURNDOWN: 24.5:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED |  | 1123.5 | 0.875 | 0.922 | 33471.4 | 29 | 31 | 983 | 1036
MLX EXT 1500 2S | B-1..B-X | MER | HEATING | CAST AL | 1343 / 1415 | 4 | 92 | -- | 2.7 | 80 | 92 | -- | -- | 56 / 113 | 7.9 FT.HD. @ 113 GPM | NATURAL GAS | 1530 | 4 - 10.5 | 120/1/60 | 10 | 38.3 x 42.8 x 57.2 | 1137 | UL/FM/CSD-1 | MH49893 | AERCO | MLX EXT 1500 2S | 2. MINIMUM TURNDOWN: 19.6:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED |  | 1530 | 0.878 | 0.925 | 33471.4 | 40 | 42 | 1343 | 1415
MLX EXT 2300 2S | B-1..B-X | MER | HEATING | CAST AL | 2015 / 2123 | 6 | 92 | -- | 4.8 | 80 | 92 | -- | -- | 84 / 169 | 16.4 FT.HD. @ 169 GPM | NATURAL GAS | 2295 | 4 - 10.5 | 120/1/60 | 15 | 38.3 x 53.3 x 57.2 | 1384 | UL/FM/CSD-1 | MH49893 | AERCO | MLX EXT 2300 2S | 2. MINIMUM TURNDOWN: 29:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED |  | 2295 | 0.878 | 0.925 | 33471.4 | 60 | 63 | 2015 | 2123
MLX EXT 2600 2S | B-1..B-X | MER | HEATING | CAST AL | 2350 / 2476 | 7 | 92 | -- | 5.9 | 80 | 92 | -- | -- | 99 / 197 | 17.8 FT.HD. @ 197 GPM | NATURAL GAS | 2677 | 4 - 10.5 | 120/1/60 | 17.5 | 38.3 x 63.9 x 57.2 | 1549 | UL/FM/CSD-1 | MH49893 | AERCO | MLX EXT 2600 2S | 2. MINIMUM TURNDOWN: 34:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED |  | 2677 | 0.878 | 0.925 | 33471.4 | 70 | 74 | 2350 | 2476
MLX EXT 3000 2S | B-1..B-X | MER | HEATING | CAST AL | 2687 / 2831 | 8 | 92 | -- | 7 | 80 | 92 | -- | -- | 113 / 225 | 13.2 FT.HD. @ 225 GPM | NATURAL GAS | 3060 | 4 - 10.5 | 120/1/60 | 20 | 38.3 x 63.9 x 57.2 | 1664 | UL/FM/CSD-1 | MH49893 | AERCO | MLX EXT 3000 2S | 2. MINIMUM TURNDOWN: 39:1 | 3. MAX NOX: 20 PPM, 3% O2 CORRECTED |  | 3060 | 0.878 | 0.925 | 33471.4 | 80 | 85 | 2687 | 2831

## Relief Valve (hidden)
RV Safety %
Design Pressure | 20%
Min Operating press | Max Operating Press | Relief Valve | BMKP EDGE Eval | BMKP EDGEii | BMK EDGEii | BMKP CMORE Eval | BMK CMORE Eval | MFC Eval
0 | 24 | 30 |  |  |  | #REF!
25 | 40 | 50 |  |  |  | #REF!
41 | 60 | 75 |  |  |  | #REF!
61 | 80 | 100 |  |  |  | #REF!
81 | 120 | 150 | 1 | 1 | 1 | #REF! | 1 | 1
121 | 150 | Consult Aerco |  |  |  | #REF!